## Slide 1: Lighting Fundamentals for Electricians
Wattsmart Training

## Slide 2: Section 1
Introduction

## Slide 3: Lighting Fundamentals for Energy Efficiency
Zach Jeffers, CALT
Outreach Specialist, Utah
Todd Wood, CEM, LC
Sr Program Services Manager, RMP

## Slide 4: Course Overview
Content:
This course will cover:
Basic lighting concepts and terminology
Types of lighting technologies (legacy vs LED)
Lighting design fundamentals
Energy codes and Lighting Power Density (LPD)
Lighting controls and energy savings
Real-world retrofit examples
Notes: Speaker Notes:
“This is an entry-level course—no engineering degree required.”
“Everything here applies directly to jobs you’re doing today.”
Emphasize: practical, not theoretical

## Slide 5: Learning Objectives
By the end of this course, you will be able to:
Define key lighting terms (lumens, footcandles, efficacy)
Identify common lighting technologies
Understand basic lighting design principles
Explain Lighting Power Density (LPD)
Identify energy-saving lighting controls
Notes: Speaker Notes:
Tie this to CE requirement (“you should leave knowing something new”)

## Slide 6: Why Lighting Matters
Lighting = 10–17% of commercial building energy use
One of the fastest ROI upgrades
Impacts:
  Safety
  Productivity
  Comfort

## Slide 7: Section 2
Lighting Basics

## Slide 8: What is Light?
Light is electromagnetic radiation
Visible spectrum: ~380–780 nm
Humans only see a small portion
Notes: Speaker Notes:
Keep simple—don’t get too physics-heavy

## Slide 9: Human Vision
Eye sensitivity peaks in green range
Poor lighting reduces performance
Good lighting improves accuracy + safety

## Slide 10: Lumens
Total light output from a source
Higher lumens = brighter source
Notes: 800 lumens ≈ household bulb

## Slide 11: Footcandles
Light level on a surface
1 footcandle = 1 lumen per square foot
Notes: Office: 30–50 fc
Warehouse: 10–30 fc

## Slide 12: Watts vs Lumens
Watts = energy used
Lumens = light produced
Key Idea: 👉 More lumens with fewer watts = better

## Slide 13: Efficacy
Efficacy: lumens per watt
Incandescent: ~10–15 lm/W
Fluorescent: ~60–90 lm/W
LED: 120–200 lm/W

## Slide 14: Color Temperature
Measured in Kelvin (K)
CCT | Appearance
3000K | Warm
4000K | Neutral
5000K | Cool

## Slide 15: CRI
Color Rendering Index (0–100)
Higher CRI = better color accuracy
Examples:
Retail: high CRI needed
Warehouse: less critical

## Slide 16: Glare
Excessive brightness causes discomfort
Reduces visibility and safety

## Slide 17: Summary of Terms
Lumens = Light output
Footcandles = Light on surface
Watts = Energy consumed
Efficacy = Efficiency
Color temperature = Light color
CRI = Lighting color acuity
Glare = Unwanted lighting reflection

## Slide 18: Section 3
Technologies

## Slide 19: Legacy Lighting
Incandescent
Fluorescent
HID (Metal Halide, HPS)

## Slide 20: Incandescent
Very low efficiency
Short lifespan
Mostly obsolete due to federal regulations

## Slide 21: Fluorescents
Requires ballast
Moderate efficiency
Common in offices

## Slide 22: HID Lighting
Metal Halide (white light)
High Pressure Sodium (yellow light)
Mercury Vapor (blue/white light)
Long warm-up time

## Slide 23: LED Lighting
Solid-state lighting
High efficiency
Long lifespan
Variety of colors

## Slide 24: LED Advantages
50–75% energy savings
50,000+ hour life
Instant on
Dimmable

## Slide 25: Technology Comparisons
Type | lm/W | Life
Incandescent | 10–15 | 1,000 hrs
Fluorescent | 60–90 | 15,000 hrs
LED | 100–180 | 50,000+ hrs

## Slide 26: Why LEDs Win
Energy savings
Maintenance savings
Better performance

## Slide 27: Where LEDs Struggle
Lamps in enclosed fixtures usually have reduced life
High ambient temperatures

## Slide 28: Section 4
Lighting Design- Right light, right place, right amount

## Slide 29: Recommended Light Levels
Space | Footcandles
Warehouse | 10–30
Office | 30–50
Parking | 1–5
Warehouse
10-30 Footcandles
Office
30-50 Footcandles
Parking
1-5 Footcandles

## Slide 30: Uniformity
Even lighting distribution
Avoid shadows and hot spots

## Slide 31: Fixture Spacing
Spacing depends on mounting height and space dimensions
Too wide = dark spots

## Slide 32: Mounting Height
Higher = Wider Spread
Lower = More Concentrated

## Slide 33: Beam Angles
Narrow = Focused
Wide = Spread Out

## Slide 34: Layout Example
Grid Layout
Even Spacing

## Slide 35: Common Mistakes
Overlighting
Underlighting
Poor spacing
Wrong color temp

## Slide 36: Section 5
Energy Codes

## Slide 37: Why Energy Codes Exist
Reduce energy use
Improve efficiency
Standardize buildings

## Slide 38: IECC Overview
IECC 2021 Energy Code applies to most projects
Sets max lighting power

## Slide 39: Lighting Power Density
LPD = watts per square foot
Used to limit energy use

## Slide 40: Example LPD Values
Space Type | Typical LPD (W/sf)
Warehouse (bulk storage) | 0.63
Warehouse (fine storage) | 0.93
Parking Garage | 0.18
Parking Lot (exterior) | typically calculated differently
Gymnasium | 1.24
Dining Area / Cafeteria | 0.89
Kitchen / Food Prep | 1.21
Lobby | 1.30
Stairwell | 0.69
Mechanical / Electrical Room | 0.42
Space Type | Typical LPD (W/sf)
Office – Open Plan | 0.82
Office – Enclosed | 0.98
Conference Room | 1.23
Classroom | 1.24
Corridor / Hallway | 0.66
Restroom | 0.98
Break Room / Lounge | 0.89
Retail Sales Area | 1.11
Retail Display | 1.60+

## Slide 41: Code vs. Reality
Many buildings
exceed code
Retrofits reduce usage

## Slide 42: Incentives
Wattsmart utility rebates
Faster ROI

## Slide 43: Section 6
Lighting Controls

## Slide 44: Why Controls Matter
Lights don’t need to be on all the time

## Slide 45: Occupancy Sensors
Turn off when empty
20–40% savings

## Slide 46: Daylight Harvesting
Adjust based on sunlight

## Slide 47: Scheduling
Turn off after hours
Scheduled sweeps
Dim at certain times

## Slide 48: Advanced Controls
Networked systems
Fixture-level control

## Slide 49: Control Savings
30-70% total savings

## Slide 50: Section 7
Wrap-up

## Slide 51: Retrofit Example
400W HID  150 W LED
60% savings

## Slide 52: Key Takeaways
LEDs dominate
Controls are critical
Code matters

## Slide 53: Quiz
What are Lumens?
What is LPD?
Name a control strategy
True/False: LEDs are most efficient